## Guideline Calculator
Safety Guideline for Indoor Airborne Transmission of COVID-19
Martin Z. Bazant
Contact: | bazant@mit.edu |  | http://www.mit.edu/~bazant
History: 6-4-2020 (v1), 7-1-2020 (v2), | 8-16-2020 (v3) posted on medrXiv 9-1-20, 9-16-2020 (v4),
This version: 11-1-2020 (v5)
For instructions, references and updates, please visit |  |  | http://www.mit.edu/~bazant/COVID-19
Reference: Martin Z. Bazant and John W. M. Bush, medRxiv preprint (2020)
"Beyond Six Feet: A Guideline to Limit Indoor Airborne Transmission of COVID-19"
https://www.medrxiv.org/content/10.1101/2020.08.26.20182824v1
Input values in the pink cells.
Physical Parameters
Floor area, A | 900 | ft2 | 83.6127 | m2
Mean ceiling height, H | 12 | ft | 3.6576 | m
Room volume, V | 10800 | ft3 | 305.8219 | m3
Outdoor air exchange rate, la | 3 | /hr (ACH)
Ventilation (outdoor air) flow rate, Q | 540 | ft3/min | 917.4658 | m3/hr
Recirculation air exchange rate, lr | 6 | /hr (ACH) | (includes HVAC & air filtration units)
Recirculation (return) flow rate, Qr | 1080 | ft3/min | 1834.9317 | m3/hr
Primary (total) air flow rate, Q+Qr | 1620 | ft3/min | 2752.3975 | m3/hr
Primary outdoor air fraction, Zp | 0.33333 | (=1.0 natural ventilation, or no recirculation)
Aerosol filtration efficiency, pf | 0.8 | (>0.9997 HEPA, =0.2-0.9 MERVs, =0 no filter)
Air filtration rate, lf | 4.8 | /hr
Relative humidity, RH | 45 | %
Physiological Parameters
Mean breathing flow rate, Qb | 0.29429 | ft3/min | 0.5 | m3/hr (=0.5 rest, =1-3 active)
Respiratory aerosol radius, r | 2 | mm | (depends weakly on activity, disease)
Humidity-adjusted radius | 1.7986 | mm
Disease Parameters
Infectiousness of exhaled air, Cq | 30 | infection quanta/m3 |  | (depends on activity, Fig. 2)
Viral deactivation rate, lv @ 50% RH | 0.3 | /hr | 3.3333 | hour deactivation time
Humidity-adjusted deactivation rate | 0.27 | /hr | (assume linear in RH)
(can increase with UV and chemical disinfectants)
Infectious Aerosol Properties
Effective settling speed, vs(r) | 0.38819 | mm/sec | 1.3975 | m/hr.
Concentration relaxation rate, lc | 8.4521 | /hr | 0.11831 | hour relaxation time
Dilution factor, fd | 0.00019344 | infectiousness of ambient air / exhaled breath
Infectiousness of room air, fd Cq | 0.0058031 | infection quanta/m3 in steady state
Precautionary Parameters
Mask aerosol passage probability, pm | 0.1 | (=1 no masks, 0.05-0.5 fabric, <0.05 surgical mask)
Airborne transmission rate, ba | 2.9015e-05 | /hr | (per pair of persons in steady state)
Risk tolerance, e | 0.05 | (bound on Rin, expected transmissions per infector)
Safe Room Occupancy
Exposure time, t | 30 | hours | (net before testing/removal/recovery)
Maximum safe occupancy, Nmax | 58 | persons | (with transient aerosol buildup)
| 58 | persons | (steady state aerosol concentration)
6 FOOT RULE (CDC) | 25 | persons
1 METER RULE (WHO) | 83 | persons
Maximum occupancy for outdoor air | 45 | persons
Minimum outdoor airflow / person | 12 | ft3/min | 5.6634 | L/s
Safe Exposure Time
Room occupancy, N | 25 | persons
Maximum exposure time, tmax | 71.9189 | hours | 4315.1359 | minutes (transient)
| 71.8008 | hours | 4308.0487 | minutes (steady state)

## Plot Data
t (hours) | N | Transient cumulative exposure time bound
0 | 10000 | epsilon | beta_a | lambda_c | N (6 ft rule) | 2.3973 | dtau
2.3973 | 755.2934 | 0.05 | 2.9015e-05 | 8.4521 | 25
4.7946 | 369.2777 | 0.05 | 2.9015e-05 | 8.4521 | 25
7.1919 | 244.5476 | 0.05 | 2.9015e-05 | 8.4521 | 25
9.5892 | 182.9216 | 0.05 | 2.9015e-05 | 8.4521 | 25
11.9865 | 146.1825 | 0.05 | 2.9015e-05 | 8.4521 | 25
14.3838 | 121.7884 | 0.05 | 2.9015e-05 | 8.4521 | 25
16.7811 | 104.4122 | 0.05 | 2.9015e-05 | 8.4521 | 25
19.1784 | 91.4065 | 0.05 | 2.9015e-05 | 8.4521 | 25
21.5757 | 81.3066 | 0.05 | 2.9015e-05 | 8.4521 | 25
23.973 | 73.2365 | 0.05 | 2.9015e-05 | 8.4521 | 25
26.3703 | 66.6402 | 0.05 | 2.9015e-05 | 8.4521 | 25
28.7676 | 61.1478 | 0.05 | 2.9015e-05 | 8.4521 | 25
31.1649 | 56.5036 | 0.05 | 2.9015e-05 | 8.4521 | 25
33.5622 | 52.5251 | 0.05 | 2.9015e-05 | 8.4521 | 25
35.9595 | 49.0788 | 0.05 | 2.9015e-05 | 8.4521 | 25
38.3568 | 46.0647 | 0.05 | 2.9015e-05 | 8.4521 | 25
40.7541 | 43.4061 | 0.05 | 2.9015e-05 | 8.4521 | 25
43.1514 | 41.0438 | 0.05 | 2.9015e-05 | 8.4521 | 25
45.5487 | 38.9308 | 0.05 | 2.9015e-05 | 8.4521 | 25
47.946 | 37.0296 | 0.05 | 2.9015e-05 | 8.4521 | 25
50.3433 | 35.3098 | 0.05 | 2.9015e-05 | 8.4521 | 25
52.7405 | 33.7468 | 0.05 | 2.9015e-05 | 8.4521 | 25
55.1378 | 32.32 | 0.05 | 2.9015e-05 | 8.4521 | 25
57.5351 | 31.0123 | 0.05 | 2.9015e-05 | 8.4521 | 25
59.9324 | 29.8095 | 0.05 | 2.9015e-05 | 8.4521 | 25
62.3297 | 28.6993 | 0.05 | 2.9015e-05 | 8.4521 | 25
64.727 | 27.6715 | 0.05 | 2.9015e-05 | 8.4521 | 25
67.1243 | 26.7173 | 0.05 | 2.9015e-05 | 8.4521 | 25
69.5216 | 25.829 | 0.05 | 2.9015e-05 | 8.4521 | 25
71.9189 | 25 | 0.05 | 2.9015e-05 | 8.4521 | 25
74.3162 | 24.2246 | 0.05 | 2.9015e-05 | 8.4521 | 25
76.7135 | 23.4977 | 0.05 | 2.9015e-05 | 8.4521 | 25
79.1108 | 22.8149 | 0.05 | 2.9015e-05 | 8.4521 | 25
81.5081 | 22.1724 | 0.05 | 2.9015e-05 | 8.4521 | 25
83.9054 | 21.5666 | 0.05 | 2.9015e-05 | 8.4521 | 25
86.3027 | 20.9945 | 0.05 | 2.9015e-05 | 8.4521 | 25
88.7 | 20.4534 | 0.05 | 2.9015e-05 | 8.4521 | 25
91.0973 | 19.9408 | 0.05 | 2.9015e-05 | 8.4521 | 25
93.4946 | 19.4545 | 0.05 | 2.9015e-05 | 8.4521 | 25
95.8919 | 18.9926 | 0.05 | 2.9015e-05 | 8.4521 | 25
98.2892 | 18.5532 | 0.05 | 2.9015e-05 | 8.4521 | 25
100.6865 | 18.1348 | 0.05 | 2.9015e-05 | 8.4521 | 25
103.0838 | 17.7359 | 0.05 | 2.9015e-05 | 8.4521 | 25
105.4811 | 17.3551 | 0.05 | 2.9015e-05 | 8.4521 | 25
107.8784 | 16.9912 | 0.05 | 2.9015e-05 | 8.4521 | 25
110.2757 | 16.6432 | 0.05 | 2.9015e-05 | 8.4521 | 25
112.673 | 16.31 | 0.05 | 2.9015e-05 | 8.4521 | 25
115.0703 | 15.9908 | 0.05 | 2.9015e-05 | 8.4521 | 25
117.4676 | 15.6845 | 0.05 | 2.9015e-05 | 8.4521 | 25
119.8649 | 15.3905 | 0.05 | 2.9015e-05 | 8.4521 | 25
122.2622 | 15.1081 | 0.05 | 2.9015e-05 | 8.4521 | 25
124.6595 | 14.8365 | 0.05 | 2.9015e-05 | 8.4521 | 25
127.0568 | 14.5752 | 0.05 | 2.9015e-05 | 8.4521 | 25
129.4541 | 14.3236 | 0.05 | 2.9015e-05 | 8.4521 | 25
131.8514 | 14.0811 | 0.05 | 2.9015e-05 | 8.4521 | 25
134.2487 | 13.8473 | 0.05 | 2.9015e-05 | 8.4521 | 25
136.646 | 13.6218 | 0.05 | 2.9015e-05 | 8.4521 | 25
139.0433 | 13.404 | 0.05 | 2.9015e-05 | 8.4521 | 25
141.4406 | 13.1935 | 0.05 | 2.9015e-05 | 8.4521 | 25
143.8379 | 12.9901 | 0.05 | 2.9015e-05 | 8.4521 | 25
146.2352 | 12.7934 | 0.05 | 2.9015e-05 | 8.4521 | 25
148.6325 | 12.6031 | 0.05 | 2.9015e-05 | 8.4521 | 25
151.0298 | 12.4187 | 0.05 | 2.9015e-05 | 8.4521 | 25
153.4271 | 12.2402 | 0.05 | 2.9015e-05 | 8.4521 | 25
155.8244 | 12.0671 | 0.05 | 2.9015e-05 | 8.4521 | 25
158.2216 | 11.8993 | 0.05 | 2.9015e-05 | 8.4521 | 25
160.6189 | 11.7365 | 0.05 | 2.9015e-05 | 8.4521 | 25
163.0162 | 11.5785 | 0.05 | 2.9015e-05 | 8.4521 | 25
165.4135 | 11.4251 | 0.05 | 2.9015e-05 | 8.4521 | 25
167.8108 | 11.2761 | 0.05 | 2.9015e-05 | 8.4521 | 25
170.2081 | 11.1312 | 0.05 | 2.9015e-05 | 8.4521 | 25
172.6054 | 10.9904 | 0.05 | 2.9015e-05 | 8.4521 | 25
175.0027 | 10.8535 | 0.05 | 2.9015e-05 | 8.4521 | 25
177.4 | 10.7202 | 0.05 | 2.9015e-05 | 8.4521 | 25
179.7973 | 10.5905 | 0.05 | 2.9015e-05 | 8.4521 | 25
182.1946 | 10.4643 | 0.05 | 2.9015e-05 | 8.4521 | 25
184.5919 | 10.3413 | 0.05 | 2.9015e-05 | 8.4521 | 25
186.9892 | 10.2214 | 0.05 | 2.9015e-05 | 8.4521 | 25
189.3865 | 10.1046 | 0.05 | 2.9015e-05 | 8.4521 | 25
191.7838 | 9.9908 | 0.05 | 2.9015e-05 | 8.4521 | 25
194.1811 | 9.8797 | 0.05 | 2.9015e-05 | 8.4521 | 25
196.5784 | 9.7713 | 0.05 | 2.9015e-05 | 8.4521 | 25
198.9757 | 9.6656 | 0.05 | 2.9015e-05 | 8.4521 | 25
201.373 | 9.5624 | 0.05 | 2.9015e-05 | 8.4521 | 25
203.7703 | 9.4616 | 0.05 | 2.9015e-05 | 8.4521 | 25
206.1676 | 9.3631 | 0.05 | 2.9015e-05 | 8.4521 | 25
208.5649 | 9.267 | 0.05 | 2.9015e-05 | 8.4521 | 25
210.9622 | 9.173 | 0.05 | 2.9015e-05 | 8.4521 | 25
213.3595 | 9.0811 | 0.05 | 2.9015e-05 | 8.4521 | 25
215.7568 | 8.9912 | 0.05 | 2.9015e-05 | 8.4521 | 25
218.1541 | 8.9034 | 0.05 | 2.9015e-05 | 8.4521 | 25
220.5514 | 8.8174 | 0.05 | 2.9015e-05 | 8.4521 | 25
222.9487 | 8.7333 | 0.05 | 2.9015e-05 | 8.4521 | 25
225.346 | 8.651 | 0.05 | 2.9015e-05 | 8.4521 | 25
227.7433 | 8.5704 | 0.05 | 2.9015e-05 | 8.4521 | 25
230.1406 | 8.4915 | 0.05 | 2.9015e-05 | 8.4521 | 25
232.5379 | 8.4143 | 0.05 | 2.9015e-05 | 8.4521 | 25
234.9352 | 8.3386 | 0.05 | 2.9015e-05 | 8.4521 | 25
237.3325 | 8.2644 | 0.05 | 2.9015e-05 | 8.4521 | 25
239.7298 | 8.1917 | 0.05 | 2.9015e-05 | 8.4521 | 25
242.1271 | 8.1205 | 0.05 | 2.9015e-05 | 8.4521 | 25
244.5244 | 8.0506 | 0.05 | 2.9015e-05 | 8.4521 | 25
246.9217 | 7.9822 | 0.05 | 2.9015e-05 | 8.4521 | 25
249.319 | 7.915 | 0.05 | 2.9015e-05 | 8.4521 | 25
251.7163 | 7.8491 | 0.05 | 2.9015e-05 | 8.4521 | 25
254.1136 | 7.7845 | 0.05 | 2.9015e-05 | 8.4521 | 25
256.5109 | 7.721 | 0.05 | 2.9015e-05 | 8.4521 | 25
258.9082 | 7.6588 | 0.05 | 2.9015e-05 | 8.4521 | 25
261.3055 | 7.5976 | 0.05 | 2.9015e-05 | 8.4521 | 25
263.7027 | 7.5376 | 0.05 | 2.9015e-05 | 8.4521 | 25
266.1 | 7.4787 | 0.05 | 2.9015e-05 | 8.4521 | 25